PROJECT SPECIFICATIONS

ALL WORK REQUIRED TO COMPLETE THIS IMPROVEMENT SHALL BE PERFORMED IN STRICT ACCORDANCE WITH THE DETAILED CONSTRUCTION PLANS AND SPECIFICATIONS, AND THE CURRENT CITY OF ALLIANCE STANDARDS AND SPECIFICATIONS.  IN THE EVENT OF A CONFLICT BETWEEN THE SPECIFICATION/REQUIREMENTS, THE MORE STRINGENT OF THE TWO WILL GOVERN, AS DETERMINED BY THE ENGINEER.  THE OHIO DEPARTMENT OF TRANSPORTATION STANDARD CONSTRUCTION DRAWINGS SHALL APPLY.

PROJECT SAFETY

THE CONTRACTOR SHALL MAINTAIN A SAFE WORKING ENVIRONMENT AT THE PROJECT SITE AT ALL TIMES.  THE CONTRACTOR SHALL PROPERLY SUPPORT AND/OR MAINTAIN ALL EXCAVATIONS PER APPLICABLE SAFETY REQUIREMENTS AND COMPLY WITH ALL OSHA REGULATIONS.  THIS SHALL INCLUDE STRICT COMPLIANCE WITH ALL APPLICABLE REGULATIONS/REQUIREMENTS REGARDING TRENCH SAFETY.  ADEQUATE BARRICADES, WARNING LIGHTS, SIGNS, FENCING, ETC., SHALL BE ERECTED AROUND THE CONSTRUCTION AREA DURING ALL NON-WORKING HOURS TO ALERT PERSONS TO THE POTENTIAL DANGER ASSOCIATED WITH THE AREA UNDER CONSTRUCTION AS WELL AS TO PREVENT ACCESS TO UNAUTHORIZED PERSONNEL TO THE CONSTRUCTION SITE.  TRENCHES SHALL BE BACKFILLED AT THE END OF EACH WORKING DAY OR PROPERLY SECURED AS APPROVED BY THE ENGINEER.  IT SHALL BE THE CONTRACTOR’S RESPONSIBILITY TO ENSURE THE SAFETY OF THE GENERAL PUBLIC AS WELL AS ALL CONSTRUCTION PERSONNEL.  PUBLIC STREETS SHALL BE KEPT CLEAN AND FREE OF DEBRIS (MUD, STONE, ETC) AT ALL TIMES.  THE CONTRACTOR SHALL CONTACT ALL LOCAL EMERGENCY AGENCIES TO THE NATURE OF THE PROPOSED PROJECT PRIOR TO BEGINNING ANY CONSTRUCTION ACTIVITY.  ACCESS FOR EMERGENCY VEHICLES SHALL BE MAINTAINED AT ALL TIMES.

UTILITY NOTIFICATION

AT LEAST TWO WORKING DAYS PRIOR TO COMMENCING OPERATIONS ON THIS PROJECT THE CONTRACTOR SHALL NOTIFY THE ENGINEER, THE REGISTERED UTILITY PROTECTION AGENCY/SERVICE, AND THE OWERS OF ANY OTHER UTILITIES (PUBLIC AND/OR PRIVATE) THAT MAY HAVE UTILITY LINES OR FACILITIES WITHIN THE VICINITY OF THIS PROJECT.  CONTACT THE OHIO UTILITIES PROTECTION SERVICE AT 1-800-362-2764.  FOR CITY OF ALLIANCE OWNED UTILITIES LOCATION CONTACT THE WATER DISTRIBUTION OFFICE AT (330) 823-5216.

PROTECTION OF UTILITIES

THE CONTRACTOR SHALL TAKE ALL PRECAUTIONS NECESSARY TO LOCATE, ISOLATE, PROTECT, AND SUPPORT ANY EXISITNG UTILITIES WITHIN OR ADJACENT TO THE PROJECT SITE WHICH MAY BE ENCOUNTERED DURING THE COMPLETION OF THE PROPOSED IMPROVEMENTS.  UTILITIES MUST BE KEPT IN SERVICE AT ALL TIMES.

TEMPORARY SEEDING AND MULCHING

THE CONTRACTOR SHALL BE RESPONSIBLE TO SEED AND MULCH WITHIN SEVEN (7) DAYS ALL DISTURBED AREAS WHERE CONSTRUCTION ACTIVITY HAS OCCURRED BUT WILL TEMPORARILY REMAIN IDLE FOR A PERIOD OF MORE THAN 30 DAYS, AND OTHER DISTURBED AREAS WHERE EROSION MAY BECOME A PROBLEM AS DETERMINED BY THE ENGINEER.  THE CONTRACTOR SHALL REFER TO THE STORMWATER PREVENTION POLLUTION PLAN FOR ADDITIONAL REQUIREMENTS.

MAINTAINING TRAFFIC

THE CONTRACTOR SHALL MAINTAIN TRAFFIC ADJACENT TO THE PROJECT AS DESCRIBED BELOW IN ACCORDANCE WITH THE REQUIREMENTS OF THE OHIO DEPARTMENT OF TRANSPORTATION MANUAL OF CONSTRUCTION AND MATERIALS SPECIFICATIONS ITEM 614 MAINTAINING TRAFFIC.  THE CONTRACTOR SHALL FURNISH & MAINTAIN ALL SIGNS, FLAGS, FLAGPERSONS, BARRICADES, SIGN SUPPORTS, CONES, BARRELS, AND INCIDENTALS IN CONFORMANCE WITH THE MOST RECENT REVISED EDITION OF THE OHIO MANUAL OF UNIFORM TRAFFIC CONTROL DEVICES FOR STRETS AND HIGHWAYS.  INTERFERENCE WITH TRAFFIC SHALL BE KEPT MINIMAL AT ALL TIMES.  ALL OPEN TRENCHES AND EXCAVATONS SHALL BE PROTECTED WITH DRUMS, BARRICADES, OR BARRIERS AT ALL TIMES.  THE CONTRACTOR MUST OBTAIN A PERMIT FROM THE CITY OF ALLIANCE FOR ROAD CLOSURES, CONTACT THE MAYOR’S OFFICE AT (330) 821-3110.

TEMPORARY SOIL EROSION AND SEDIMENT CONTROL

THE CONTRACTOR SHALL PREVENT AND/OR REDUCE AND CONTROL SOIL EROSION RESULTING FROM THE PROPOSED IMPROVEMENTS.  THE USE OF SILT FENCING, JUTE MATTING, TEMPORARY SEEDING, SILT CHECKS, INLET PROTECTION AROUND CATCH BASINS, STABILIZED CONSTRUCTION ENTRANCE(S), ETC. WILL BE REQUIRED.  SEDIMENT CONTROL STRUCTURES/DEVICES SHALL BE INSTALLED IN ACCORDANCE WITH THE MAUAL RAINWATER AND LAND DEVELOPMENT – OHIO’S STANDARDS FOR STORM WATER MANAGEMENT, LAND DEVELOPMENT AND URBAN STREAM PROTECTION, SECOND EDITION DATED 1996.  SEDIMENT CONTROL DEVICES MUST BE INSTALLED PRIOR TO BEGINNING ANY CONSTRUCTION ACTIVITY.  THE CONTRACTOR SHALL BE RESPONSIBLE FOR CONTINUED INSPECTION AND MAINTENANCE OF ALL SEDIMENT CONTROL DEVICES.  THE CONTRACTOR SHALL FOLLOW THE REQUIREMENTS SET FORTH ON THE APPROVED STORM WATER POLLUTION PREVENTION PLAN IF APPLICABLE OR ON THE DETAILED CONSTRUCTION PLANS, AS SPECIFIED BY THE CITY OF ALLIANCE.

A PERMIT WITH THE EPA FOR STORM WATER POLLUTION PREVENTION MUST BE OBTAINED.  THE CITY MUST RECEIVE A LETTER FROM THE STARK SOIL AND WATER CONSERVATION DISTRICT STATING THAT A SWP3 PLAN HAS BEEN REVIEWED AND APPROVED FOR THIS PROJECT PRIOR TO THE CITY’S APPROVAL

RESTORATION OF DISTURBED AREAS

EXISTING DRIVES, BERMS, LAWNS, PAVEMENTS, CURBS, SIDEWALKS, SIGNS, MAILBOXES, OR OTHER APPURTENANCES DISTURBED DURING CONSTRUCTION BUT NOT SPECIFICALLY DESIGNATED FOR REMOVAL/REPLACEMENT SHALL BE RESTORED TO A CONDITION EQUAL TO THAT WHICH EXISTED PRIOR TO CONSTRUCTION AND TO THE COMPLETE SATISFACTON OF THE CITY ENGINEER.  RESTORATION OF EXISITNG ROADWAYS SHALL BE IN ACCORDANCE WITH THE GOVERING AGENCY HAVING AUTHORITY.  THE COST FOR THE RESTORATION OF THESE ITEMS SHALL BE SOLELY THE CONTRACTORS RESPONSIBILITY.  NO PUBLIC ROADWAY SHALL BE DISTURBED WITHOUT PRIOR WRITTEN APPROVAL OF THE CITY ENGINEER AND HAVING ALL APPLICIBLE PERMITS OBTAINED.

EASEMENTS AND RIGHT OF WAYS

THE CONTRACTOR SHALL STAY WITHIN THE PROPERTIES, EASEMENTS, WORK LIMITS, AND RIGHTS OF WAY PROVIDED AT ALL TIMES.  NO MATERIAL IS PERMITTED TO BE STORED ON ADJACENT PROPERTIES UNLESS PRIOR WRITTEN PERMISSION HAS BEEN GRANTED.  

WATER MAINS/SERVICES

WATER MAINS SHALL BE CLASS 52, DUCTILE IRON PIPE MEETING AWWA C-151 WITH PUSH ON JOINTS AND “K” COPPER MAY BE USED FOR SERVICE CONNECTIONS.  THE MINIMUM COVER OVER WATER MAINS SHALL BE 5 FEET FROM THE FINSIHED GRADE SURFACE TO THE TOP OF THE PIPE.  THE OUTSIDE SURFACE OF ALL DUCTILE IRON PIPE, FITTINGS AND APPURTENANCES SHALL BE SHOP COATED WITH EITHER A COAL TAR OR ASPHALT BASE BITUMINOUS MATERIAL.  IF THIS COATING MATERIAL IS FOUND TO BE DAMAGED PRIOR TO THE PIPE TRENCH BEING BACKFILLED, THE CONTRACTOR SHALL PROVIDE AN ADDITIONAL APPROVED MATERIAL AS REQUIRED TO REPAIR THE DAMAGES.  THE INTERIOR OF ALL PIPES AND FITTINGS SHALL BE LINED WITH CEMENT MORTAR AND SEAL COATED IN COMPLETE CONFORMANCE WITH AWWA C-104, OR THE LATEST REVISION.  FITTINGS SHALL BE RATED FOR 250 PSI WORKING PRESSURE IN ACCORDANCE WITH AWWA C-110.  PIPE LENGTHS MAY BE DEFLECTED AT THE JOINTS IF REQUIRED, AT ONE-HALF THE DEGREE RECOMMENDED BY THE MANUFACTURER.  DISINFECTION OF WATER MAINS SHALL BE IN ACCORDNACE WITH AWWA C-651.  ALL WATER LINE PRESSURE TESTING SHALL CONFORM TO AWWA C-600, AND THE REQUIREMNTS AND/OR SPECIFICATIONS OF THE CITY OF ALLIANCE WATER DISTRIBUTION DEPARTMENT.  WATER MAINS SHALL BE INSTALLED PER ODOT ITEM 603 AS TYPE B OR C CONDUITS.  WATER LINES AND SERVICES LOCATED WITHIN THE LIMITS OF OR WITHIN A 1 TO 1 SLOPE OF EXISITNG AND/OR PROPOSED ROADWAYS, SIDEWALKS, AND/OR DRIVES SHALL BE INSTALLED AS TYPE B CONDUITS.  ALL OTHER WATER MAINS/SERVICES MAY BE INSTALLED AS TYPE C CONDUITS.

ALL BENDS, FITTINGS, TEES, VALVES, DEAD ENDS, ETC., SHALL BE SECURED/RESTRAINED USING MECHANICAL JOINT RESTRAINT, MEGALUG OR APPROVED EQUAL. WOODEN THRUST BLOCKS SHALL ALSO BE PROVIDED AT/FOR EACH BEND, FITTING, TEE, DEAD END, ETC.  THIS BLOCKING SHALL BE CAREFULLY PLACED TO ENSURE THAT IT IS POSITIONED PROPERLY TO WITHSTAND THE RESULTANT FORCES AT EACH BEND, FITTING, ETC., AND SHALL BEAR ON STABLE UNDISTURBED GROUND CAPABLE OF WITHSTANDING THE POTENTIAL LOADING.  IN ADDITION, TO THE RESTRAINT OF ALL BENDS, FITTINGS, TEES, VALVES, DEAD ENDS, ETC., THE CONTRACTOR SHALL ALSO SECURE/RESTRAIN ALL JOINTS WITH 50 LF MIN OF EACH DEAD END, BEND, FITTING, VALVE, TEE, ETC., UTILIZING MEGALUGS, FIELD LOK GASKETS, OR APPROVED EQUAL.

THE CONTRACTOR SHALL MAINTAIN 18” VERTICAL CLEARANCE BETWEEN PROPOSED WATER LINES AND ANY STORM/SANITARY SEWERS.  WHEN 18” CANNOT BE OBTAINED, THE CONTRACTOR SHALL PROVIDE CONCRETE ENCASEMENT AS DIRECTED BY THE ENGINEER.  THE CONTRACTOR SHALL MAINTAIN 10 FEET HORIZONTAL CLEARANCE BETWEEN WATERLINES/SERVICES AND SANITARY/STORM SEWERS.

WATERLINES SHALL BE INSTALLED IN SUCH A MANNER AS TO AVOID LOCALIZED HIGH POINTS.

ALL WATER VALVES SHALL MEET THE REQUIREMENTS OF AWWA C509 OR C515 AND SHALL OPEN RIGHT AND MEET THE REQUIREMENTS OF THE CITY OF ALLIANCE WATER DISTRIBUTION DEPARTMENT.

FIRE HYDRANTS SHALL BE MUELLER CENTURIAN 200 WITH 4-1/2 INCH NOZZLES WITH ALL VALVES OPENING RIGHT AND MEET THE REQUIREMENTS OF THE CITY OF ALLIANCE WATER DISTRIBUTION DEPARTMENT.

35 PSI MINIMUM SHALL BE MAINTAINED TO THE CURB STOP DURING NORMAL OPERATING CONDITIONS.

BOOSTER PUMPS ARE NOT PERMITTED ON SERVICE LINES.

ALL WATERLINES GREATER THAN 2” MUST PASS A CITY PRESSURE AND BACTERIA TEST.  CONTACT THE CITY OF ALLIANCE WATER DISTRIBUTION DEPARTMENT AT (330) 823-5216 WHEN TESTING IS READY.

UTILITY SERVICES

THE CONTRACTOR SHALL PROPERLY AND ADEQUATELY SECURE PLUGS ON THE ENDS OF ALL STORM, WATER, AND SANITARY SERVICES/LATERALS.  THE CONTRACTOR SHALL MARK THE ENDS OF EACH LATERAL/SERVICE WITH A 2X2 OAK STAKE, EXTENDING 3 FEET ABOVE FINISHED GRADE.  THE 2X2 STAKES SHALL BE COLOR COORDINATED TO DESIGNATE THE DIFFERENT LATERAL/SERVICE.

SANITARY SEWERS

ALL SANITARY SEWERS AND LATERALS SHALL BE PVC SDR-35 MEETING REQUIREMENTS OF ASTM D-3034 WITH JOINTS MEETING ASTM D-3212.  MINIMUM COVER OVER SANITARY SEWERS SHALL BE 4 FEET.

SANITARY SEWERS AND LATERALS SHALL BE INSTALLED PER ODOT ITEM 603 AS TYPE B OR TYPE C CONDUITS.  SANITARY SEWERS AND LATERALS LOCATED WITHIN THE LIMITS OF OR WITHIN A 1 TO 1 SLOPE OF EXISTING/PROPOSED ROADWAYS, SIDEWALKS, AND/OR DRIVES SHALL BE INSTALLED AS TYPE B CONDUITS.  ALL OTHER SANITARY SEWERS MAY BE INSTALLED AS TYPE C CONDUITS.  SEE PIPE BEDDING DETAIL FOR BEDDING REQUIREMENTS.

DEFLECTING TESTING OF ALL SANITARY SEWERS SHALL BE CONDUCTED 30 DAYS AFTER INSTALLATION AND BACKFILLING OF THE PIPE OR AS OTHERWISE DIRECTED BY THE CITY ENGINEER.  THE ALLOWABLE DEFLECTION RATE SHALL NOT EXCEED 5%.  TESTING SHALL BE IN ACCORDANCE WITH ASTM D-3034.

EXFILTRATION TESTING (OR INFILTRATION IF APPLICABLE) SHALL NOT EXCEED A MAXIMUM ALLOWABLE LEAKAGE OF 100 GALLON/INCH OF PIPE DIAMETER/MILE/DAY.  IN LIEU OF SAID WATER TESTS, A LOW PRESSURE AIR TEST MAY BE CONDUCTED PER RECOMMENDED STANDARDS FOR SEWAGE WORKS (TEN STATE STANDARDS).  THE PROPOSED SANITARY SEWER SYSTEMS SHALL BE TESTED, APPROVED, AND ACCEPTED PRIOR TO BEING PUT INTO SERVICE.

THE CONTRACTOR SHALL BE RESPONSIBLE FOR PROPERLY MAINTAINING ANY EXISITNG SANITARY FLOW DURING THE COMPLETION AND/OR TESTING OF SAID IMPROVMENTS.

IF NEEDED THE CONTRACTOR SHALL CAREFULLY AND ACURATELY CORE DRILL ANY REQUIRED OPENINGS INTO EXISTING MANHOLES AND PROVIDE A WATERTIGHT CONNECTION.  BENCHES AND CHANNELS SHALL BE REPAIRED AS NECESSARY.

IF PROPOSED SANITARY SEWER MANHOLES WILL BE CONTRUCTED OVER EXISTING SANITARY SEWERS, BULKHEADS SHALL BE PLACED WITHIN THE PROPOSED LINE AND SHALL REMAIN IN PLACE UNTIL THE PROPOSED SANITARY SEWER HAS BEEN COMPLETED, TESTED AND APPROVED.

MANHOLE CONSTRUCTION SHALL MEET THE REQUIREMENTS OF ASTM C-478 AND C-443.  MANHOLES SHALL BE LEAKAGE (AIR/VACUUM) TESTED IN ACCORDANCE WITH AND MEET ALL REQUIREMENTS OF ASTM C-1244.

MINIMUM VERTICAL CLEARANCE BETWEEN SANITARY SEWERS AND WATER LINES SHALL BE 18” AND HAVE A HORIZONTAL SEPARATION (OUT TO OUT) OF 10 FEET.

ROOF DRAINS, FOUNDATION DRAINS, AND OTHER CLEAN WATER CONNECTIONS TO A SANITARY SEWER ARE PROHIBITED.

TESTING OF UTILITIES

ALL WATERLINES AND SANITARY SEWERS (INCLUDING LATERALS) MUST BE INSTALLED AND TESTED IN ACCORDANCE WITH APPLICABLE STANDARDS (AWWA, ETC.), PER THE OHIO ENVIRONMENTAL PROTECTION AGANCY, AND PER THE LOCAL GOVERNING AGENCY HAVING AUTHORITY BEFORE THEY WILL BE ACCEPTED.  THIS WILL INCLUDE DISENFECTION AND PRESSURE TESTING OF WATERLINES AND SERVICES.  SANITARY SEWERS SHALL BE SUBJECTED TO LEAKAGE TESTING WHICH WOULD INCLUDE APPROPRIATE WATER (EXFILTRATION/INFILTRATION) OR LOW PRESSURE AIR TESTING.  DEFLECTION TESTING WILL BE REQUIRED OF ALL FLEXIBLE CONDUIT/PIPE (PVC) AND SHALL BE PERFORMED 30 DAYS AFTER INSTALLATION OF THE PIPE.  DEFLECTION TESTING AND LEAKAGE TESTING MUST BE PERFORMED PERIODICALLY AS WORK PROGRESSES AND AS SOON AS TIME RESTRAINTS ALLOW (DEFLECTION TESTING) AND AT THE DIRECTION OF THE CITY ENGINEER.

DEFLECTION TESTING OF FLEXIBLE CONDUIT SHALL BE CONDUCTED THIRTY (30) DAYS AFTER INSTALLATION AND BACKFILLING OF THE PIPE OR AS DIRECTED BY THE ENGINEER.  THE CONTRACTOR SHALL FURNISH ALL NECESSARY EQUIPMENT INCLUDING AN APPROVABLE MANDREL OR OTHER APPROVED DEVICE AND CONDUCT THE DEFLECTION TESTS AT THE DIRECTION OF THE ENGINEER.  THE ALLOWABLE DEFLECTION RATE SHALL NOT EXCEED 5%.  THE ENGINEER HAS THE OPTION TO REQUIRE A SECOND TEST ANYTIME BETWEEN INITIAL TESTING AND FINAL ACCEPTANCE.  ANY SECTIONS FOUND TO HAVE A DEFLECTION IN EXCESS OF THE SPECIFIED RATE SHALL BE EXCAVATED AND CORRECTED EITHER BY RE-BEDDING, PIPE REPLACEMENT OR BOTH AND DIRECTED/APPROVED BY THE ENGINEER.  THESE CORRECTIONS SHALL BE REQUIRED IF WARRENTED BY EITHER INTIAL OR SECONDARY TESTING.

ALL GRAVITY SEWERS, EIGHT (8) INCHES AND LARGER IN DIAMETER, SHALL BE SUBJECTED TO INTERNAL TEVELESION INSPECTION AFTER CONSTRUCTION AND DEFLECTION TESTING IS COMPLETE.  IT IS REQUIRED THAT THE SEWER LINES THAT ARE TO BE TELEVISED, ARE CLEANED AND FLUSHED NO MORE THAN FORTY-EIGHT (48) HOURS BEFORE TAPING OCCURS.  ALL VIDEO RECORDINGS SHALL BE DONE IN COLOR ON VHS ½ INCH TAPE CASSETES SHOWING CONTINUOUS COVERAGE OF THE SANITARY SEWER FROM MANHOLE TO MANHOLE.  THE VIDEO RECORDING SHALL BE SUPPLIED ON T-120 TAPES RECORDED AT “SP” STANDARD PLAY SPEED.  THE CAMERA TRAVEL AND VIEW SHALL BE UPSTREAM SO THAT THE BUTT-ENDS OF THE SPIGOT WILL SHOW CLEARLY.  THE VIDEO INSPECTION SEQUENCE SHALL BE FROM THE LOWEST MANHOLE TO THE FARTHEST UPSTREAM “DEAD-END” MANHOLE.  EACH SUBSEQUENT BRANCH SHALL BE RECORDED FROM A MANHOLE ALREADY TAPED TO THE DEAD-END MANHOLE OF THE BRANCH.  ALL INTERNAL INSPECTION SHALL BE DONE BY PERSONS AND/OR FIRMS QUALIFIED AND APPROVED BY THE ENGINEER.  COMPLETED VIDEO RECORDINGS SHALL BE GIVEN OT THE CITY OF ALLIANCE ENGINEERING DEPARTMENT.

STORM SEWERS

ALL PROPOSED STORM SEWERS SHALL MEET THE REQUIREMENTS OF ODOT ITEM 603 FOR TYPE B OR TYPE C CONDUITS. STORM SEWERS LOCATED WITHIN THE LIMITS OF OR WITHIN A 1 TO 1 SLOPE OF EXISTING/PROPOSED ROADWAYS, SIDEWALKS, AND/OR DRIVES SHALL BE INSTALLED AS TYPE B CONDUITS.  ALL OTHER STORM SEWERS MAY BE INSTALLED AS TYPE C CONDUITS.  THE CONTRACTOR SHALL USE RCP OR HDPE/HDPP ONLY WITH A MINIMUM DIAMETER OF 12” WITHIN THE CITY’S RIGHT OF WAY.  MIXING TYPE OF PIPE MATERIALS IN A PARTICULAR RUN IS NOT ALLOWED.  SEE TRENCH BEDDING DETAIL FOR BEDDING REQUIREMENTS.

CATCH BASINS AND STORM MANHOLES

ALL STORM SEWER CATCH BASINS AND MANHOLES SHALL MEET THE REQUIREMENTS OF ODOT ITEM 604.  PIPE OPENINGS SHALL BE PRECAST INTO ALL CATCH BASINS AND MANHOLES KNOCKOUT PANELS/SIDES ARE UNACCEPTABLE.  CATCH BASINS WITHIN THE CITY RIGHT OF WAY SHALL BE OF TYPE MODIFIED CB 3A, WITH EJIW 7030 FRAME, T4 BACK, AND M6 GRATE. 
CATCH BASINS MUST BE PRECAST OR CONSTRUCTED WITH CONCRETE BRICK MEETING ODOT 704.03.  CONCRETE MASONRY BLOCKS ARE NOT ACCEPTABLE.  IF CATCH BASINS ARE NOT PRECAST AN APPROVED WATERPROOF SEALANT MUST BE APPLIED TO THE INTERIOR AND EXTERIOR ON THE CATCH BASIN. 

INSPECTION

A PERMIT MUST BE OBTAINED FROM THE CITY OF ALLIANCE PRIOR TO ANY WORK BEING PERFORMED.  THE CONTRACTOR MUST NOTIFY THE CITY OF ALLIANCE ENGINNERING OFFICE AT (330) 823-5122 48 HOURS PRIOR TO ANY CONSTRUCTION INSIDE THE CITY’S RIGHT OF WAY IN ORDER TO COORDINATE INSPECTION.  INSPECTION DAYS AND TIMES SHALL BE M-F 8:30-4:30. 

STABLIZATION  - SEEDING AND MULCHING

ALL AREAS DISTURBED DURING CONSTRUCTION (INCLUDING EXPOSED SURFACES OF THE EMBANKMENT, EXCAVATION, SPOIL AND BORROW AREAS, BERMS, ETC.), SHALL BE STABILIZED BY SEEDING, LIMING, FERTILIZING, MULCHING, ETC., IN ACCORDANCE WITH ODOT ITEM 659, SEEDING AND MULCHING AND AS SPECIFIED ON THE STORM WATER POLLUTION PREVENTION PLAN.  STABILIZATION SHALL OCCUR WITHIN SEVEN (7) DAYS FOLLOWING THE COMPLETION OF THE IMPROVEMENTS.

PAVEMENT
JOINTS BETWEEN FACE OF CURB AND ASPHALT PAVEMENT MUST BE SEALED WITH JOINT SEALER PER ODOT 705.04.

PROOF ROLLING

PROOF ROLLING SHALL BE PERFORMED IN ACCORDANCE WITH THE OHIO DEPARTMENT OF TRANSPORTATION CONSTRUCTION AND MATERIAL SPECIFICATIONS ITEM 203.14 ON THE PREPARED COMPACTED SUBGRADE OF THE PROPOSED ROADWAY PRIOR TO PLACEMENT OF ANY ROADWAY BASE MATERIAL (ODOT ITEM 304).  THE PROOF ROLLING SHALL BE PERFORMED IN THE PRESENCE OF THE SITE GEOTECHINICAL ENGINEER AND THE CITY OF ALLIANCE ENGINEER USING A FULLY LOADED TANDEM AXLE DUMP TRUCK.  THE PROOF ROLLING OPERATION SHALL COVER THE ENTIRE WIDTH AND LENGTH OF THE PROPOSED ROADWAY.  THE PURPOSE OF THIS PROCEEDURE IS TO DETECT SOFT, YIELDING, AND/OR UNSTABLE ZONES WITHIN THE SUBGRADE.  ANY SUCH ZONES THAT ARE FOUND SHALL BE CORRECTED.  THE UNSATISFACTORY AREAS SHALL BE UNDERCUT AND REPLACED WITH CLEAN APPROVED MATERIAL, OR OTHERWISE STABILIZED/CORRECTED AS APPROVED/DIRECTED BY THE GEOTECHNICAL ENGINEER.  NO ADDITIONAL PAYMENT WILL BE MADE TO THE CONTRACTOR FOR CORRECTION OF UNACCEPTABLE AREAS.

